OSHMI
Open Substation HMI
S7 Client Protocol Driver
Configuration Manual
Version 0.1
© 2014-2019 Ricardo L. Olsen

Introduction
This driver uses the SHARP7/SNAP7 project by Davide Nardella from:
https://sourceforge.net/projects/snap7/
Using this driver it is possible to connect OSHMI to “n” PLC, RTU’s or other generic IED’s with the Siemens S7 protocol.
This driver is not a gateway, it only directs data to OSHMI.
The driver is build with the DOTNET CORE 3.0 framework, so it requires a compatible updated OS/environment.
Configuration
To understand the configuration parameters of this protocol is important to study also the SHARP7 documentation from the protocol library. Each type of PLC has it’s own connection parameters, please refer to the SHARP7 documentation.
The driver config file is c:\oshmi\conf\s7client.ini. This file has the following format:
; Define S7 server IED
[RTU_1]
IP=127.0.0.1
CONNECTION_TYPE=2
RACK=0
SLOT=0
LOCAL_TSAP=0x200
REMOTE_TSAP=0x200
PASSWORD=

; Read data from PLC and send to OSHMI points
; DATA_TYPE AREA DB OFFSET AMOUNT OSHMI_POINT_NUMBER DELAY_MS
READ_1=BYTE 0x84 1 0x0000 5 60001	0
READ_2=BIT 0x84 1 0x0010 5 81000	0
READ_3=WORD 0x84 1 0x0010 1 60000	0
READ_4=DWORD 0x84 1 0x0030 5 83000	0
READ_5=REAL 0x84 1 0x0040 5 84000	0
READ_6=COUNTER 0x1C 0 0x0000 5 85000	0
READ_7=TIMER 0x1D 0 0x0000 5 86000	1000

; Write OHSMI point value to PLC
; DATA_TYPE AREA DB OFFSET OSHMI_POINT_NUMBER BIT
WRITE_1=BIT 0x84 1 0x0000 64150 0
WRITE_2=BYTE 0x84 1 0x0000 64162 0
WRITE_3=REAL 0x84 1 0x0701 90001 0
WRITE_4=WORD 0x84 1 0x0010 94000 0
...
[RTU2]
…

Multiple slaves (servers) can be defined in the configuration file [RTU_1], [RTU_2], [RTU_N], …
For each slave there are a read and a write list.
Read lists are queues of data gathering. Each read define a range of reads from the slave to be transfered from the PLC to OSHMI. The PLC read must define the data type (BIT, BYTE, WORD, DWORD, INT, DINT, REAL, COUNTER or TIMER), the area, database (if not a database area, this parameter is ignored), starting offset for the data and amount. It must be provided the initial OSHMI point number to transfer the data (point numbers must be in sequence for each read).
Write lists define area to be written when an OSHMI command is issued. Just one value is written for each command. The OSHMI point number parameter define the OSHMI command point that will be captured and the value will be written to the PLC area/db/offset, using the specified data type.