OSHMI
Open Substation HMI
Modbus TCP Driver
Configuration Manual
Version 1.12
© 2018-2022 Ricardo L. Olsen
3. Introduction
This driver is based on libmodbus protocol stack from:
http://libmodbus.org/
Using this driver it is possible to connect OSHMI to “n” PLC’s, meters, RTU’s or other generic IED’s that can support Modbus TCP or Serial protocol.
This driver is not a gateway, it only directs data to OSHMI.
Configuration
The driver modbus.exe file is installed in c:\oshmi\bin\. This executable must be configured to run in mon_proc.ini or be executed manually.
The driver config file is c:\oshmi\conf\modbus_queue.ini. This file has the following format:

;[I104M]
; UDP Port to listen I104M transport messages (commands)
; Default=8098 (use 0 to disable commands)
;UDP_PORT_LISTEN=8098

; Define a Modbus slave IED
[RTU_1]
; IP ADDRESS
IP=127.0.0.1
; TCP PORT
PORT=502
; Slave selector (can be commented if a gateway is not used)
; SLAVE_ID=1
; Response timeout in ms
TIMEOUT=1000
; delay after each interrogation (in milliseconds)
DELAY=1000
; read holding registers (FC=0x03): mb_address, number of registers, OSHMI_address of 1st
; Analog 16bit values are converted to float and divided by 32767.0 (1FFFh -> 1.0),
; so use kconv1=32767.0 in point_list.txt to restore the value as decimal from modbus
; or scale the values as needed using kconv1(multiplier) and kconv2(offset).
READHR_1=40001 5 1000
READHR_2=40010 10 2000
; read each pair of consecutive holding registers (FC=0x03) as floats: mb_address, number of floats, OSHMI_address of 1st
READHR_FLOAT_1=60001 5 11000
READHR_FLOAT_2=60010 10 12000
; read each pair of consecutive input registers (FC=0x04) as floats: mb_address, number of floats, OSHMI_address of 1st
READIR_FLOAT_1=30101 5 30100
; read each pair of consecutive holding registers (FC=0x03) as longs: mb_address, number of floats, OSHMI_address of 1st
READHR_LONG_1=60050 1 13000
READHR_LONG_2=60052 10 14000
; read input registers (FC=0x04): mb_address, number of registers, OSHMI_address of 1st
; Analog 16bit values are converted to float and divided by 32767.0 (1FFFh -> 1.0),
; so use kconv1=32767.0 in point_list.txt to restore the value as decimal from modbus
; or scale the values as needed using kconv1(multiplier) and kconv2(offset).
READIR_1=30001 5 3000
READIR_2=30006 1 3006
; read input status (FC=0x02): mb_address, number of bits, OSHMI_address of 1st
READIS_1=10001 32 5000
; read coils status (FC=0x01): mb_address, number of bits, OSHMI_address of 1st
READCS_1=1 32 8000

; read holding registers (FC=0x03) as bistring: mb_address, number of registers, OSHMI_address of 1st
; Each register (16bit) translates to 16 consecutive digital points of OSHMI
; If read more than one register it must be created blocks of 16 digital points in point_list.txt
; All digital points must be consecutive
READHR_BITSTR_1=0 1 9000

; Define a second Modbus slave IED
[RTU_2]
IP=127.0.0.1
PORT=503
SLAVE_ID=2
TIMEOUT=500
; delay after each interrogation (in milliseconds)
DELAY=100
; read holding registers (FC=0x03): mb_address, number of registers, OSHMI_address of 1st
READHR_1=40001 5 11000
READHR_2=40010 10 12000
; read input registers (FC=0x04): mb_address, number of registers, OSHMI_address of 1st
READIR_1=30001 5 13000
READIR_2=30006 1 13006
; read input status (FC=0x02): mb_address, number of input bits, OSHMI_address of 1st
READIS_1=10001 32 15000
; read coils status (FC=0x01): mb_address, number of input bits, OSHMI_address of 1st
READCS_1=1 32 18000
…
; when there are just 2 parameters per line, OSHMI address will be the same as mb_address
; A Modbus RTU (serial) slave IED
[RTU_3]
SERIAL_PORT_NAME=COM3
BAUD_RATE=9600
DATA_BITS=8
STOP_BITS=1
PARITY=NONE
LOG_LEVEL=1
DELAY=1000
SLAVE_ID=1
TIMEOUT=1500
READIR_1=0 8 3040
READIR_2=10 4 3050
READIR_3=20 5 3060

; A Modbus RTU (serial) slave IED RS485
[RTU_4]
RS485_MODE=1
RTS_MODE=0
RTS_DELAY=20
SERIAL_PORT_NAME=COM4
BAUD_RATE=9600
DATA_BITS=8
STOP_BITS=1
PARITY=NONE
LOG_LEVEL=1
DELAY=1000
SLAVE_ID=1
TIMEOUT=1500
READIR_1=0 8 3040
READIR_2=10 4 3050
READIR_3=20 5 3060

; A Modbus RTU (serial) slave IED RS485 (on same channel as previous slave)
[RTU_5]
RS485_MODE=1
RTS_MODE=0
RTS_DELAY=20
SERIAL_PORT_NAME=COM4
BAUD_RATE=9600
DATA_BITS=8
STOP_BITS=1
PARITY=NONE
LOG_LEVEL=1
DELAY=1000
SLAVE_ID=2
TIMEOUT=1500
READIR_1=0 8 3040
READIR_2=10 4 3050
READIR_3=20 5 3060

In the point_list.txt file must be configured point numbers, addresses as OSHMI_address (or mb_address when OSHMI_address omitted), RTU column as the RTU number from modbus_queue and conversion factors (kconv’s) as needed.
Analog values from Modbus are sent to OSHMI emulating an IEC104 type 9 format (normalized value). Integer 16 bit values are divided by 32767 and converted to float (the value 32767=7FFFh represents the float value 1.0). So to restore the value as Modbus 16 bit integer you must use kconv1=32767 and kconv2=0 in point_list.txt. Use kconv1(multiplier) and kconv2(offset) to adjust the scale to your measurement as needed.
Commands are only programmed in the c:\oshmi\conf\point_list.txt as follows:
ADDR column = Modbus object address.
RTU column = sequential number (1...N) of RTU from modbus_queue.ini.
KCONV1 column = bit number (0-15) for holding register command as bitstring
ASDU column must be configured according to the command type:
Command type	Modbus	ASDU
Binary command	Single Coil, FC=0x05	45
Binary double command	Multiple Coils, FC=0x0F	46
Analog output, normalized 16 bits	Preset Single Register, FC=0x06	48
Analog output, scaled 16 bits	Preset Single Register, FC=0x06	49
Binary command as bitstring	Holding Register as bitstring, FC=0X06	64

The “Binary command as bitstring” (ASDU 64) will translate in Modbus to a holding register read (16bit register) in specified address, next only the bit numbered by KCONV1 will be masked and set/reset by the command value, then the result will be written to the same holding register. So the other 15 bits will preserve the current values.
For Modbus commands, to write to address 0 (zero) it is necessary to put in the column ADDR of point_list.txt the value “-1” (minus one). This is necessary because the value 0 (zero) in this column means that the address is the same as point number.

Sample point_list.txt file configuration:

VERSION 3
POINT_NUMB ADDR ID TYP MESSAGE ALM EQ INF OR UN RTU ASDU KCONV1 KCONV2 SUPCMD DC PR INIVAL "SUBST~BAY~DESCRIPTION"
  1000 0 MODBUS_RTU1_HR40001 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40001"
  1001 0 MODBUS_RTU1_HR40002 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40002"
  1002 0 MODBUS_RTU1_HR40003 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40003"
  1003 0 MODBUS_RTU1_HR40004 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40004"
  1004 0 MODBUS_RTU1_HR40005 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40005"
  2000 0 MODBUS_RTU1_HR40010 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40010"
  2001 0 MODBUS_RTU1_HR40011 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40011"
  2002 0 MODBUS_RTU1_HR40012 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40012"
  2003 0 MODBUS_RTU1_HR40013 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40013"
  2004 0 MODBUS_RTU1_HR40014 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40014"
  2005 0 MODBUS_RTU1_HR40015 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40015"
  2006 0 MODBUS_RTU1_HR40016 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40016"
  2007 0 MODBUS_RTU1_HR40017 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40017"
  2008 0 MODBUS_RTU1_HR40018 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40018"
  2009 0 MODBUS_RTU1_HR40019 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 40019"
  3000 0 MODBUS_RTU1_IR30001 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 30001"
  3001 0 MODBUS_RTU1_IR30002 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 30002"
  3002 0 MODBUS_RTU1_IR30003 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 30003"
  3003 0 MODBUS_RTU1_IR30004 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 30004"
  3004 0 MODBUS_RTU1_IR30005 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 30005"
  3006 0 MODBUS_RTU1_IR30006 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Holding Register 30006"
  5000 0 MODBUS_RTU1_IS10001 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10001"
  5001 0 MODBUS_RTU1_IS10002 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10002"
  5002 0 MODBUS_RTU1_IS10003 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10003"
  5003 0 MODBUS_RTU1_IS10004 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10004"
  5004 0 MODBUS_RTU1_IS10005 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10005"
  5005 0 MODBUS_RTU1_IS10006 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10006"
  5006 0 MODBUS_RTU1_IS10007 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10007"
  5007 0 MODBUS_RTU1_IS10008 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10008"
  5008 0 MODBUS_RTU1_IS10009 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10009"
  5009 0 MODBUS_RTU1_IS10010 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10010"
  5010 0 MODBUS_RTU1_IS10011 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10011"
  5011 0 MODBUS_RTU1_IS10012 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10012"
  5012 0 MODBUS_RTU1_IS10013 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10013"
  5013 0 MODBUS_RTU1_IS10014 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10014"
  5014 0 MODBUS_RTU1_IS10015 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10015"
  5015 0 MODBUS_RTU1_IS10016 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10016"
  5016 0 MODBUS_RTU1_IS10017 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10017"
  5017 0 MODBUS_RTU1_IS10018 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10018"
  5018 0 MODBUS_RTU1_IS10019 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10019"
  5019 0 MODBUS_RTU1_IS10020 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10020"
  5020 0 MODBUS_RTU1_IS10021 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10021"
  5021 0 MODBUS_RTU1_IS10022 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10022"
  5022 0 MODBUS_RTU1_IS10023 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10023"
  5023 0 MODBUS_RTU1_IS10024 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10024"
  5024 0 MODBUS_RTU1_IS10025 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10025"
  5025 0 MODBUS_RTU1_IS10026 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10026"
  5026 0 MODBUS_RTU1_IS10027 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10027"
  5027 0 MODBUS_RTU1_IS10028 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10028"
  5028 0 MODBUS_RTU1_IS10029 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10029"
  5029 0 MODBUS_RTU1_IS10030 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10030"
  5030 0 MODBUS_RTU1_IS10031 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10031"
  5031 0 MODBUS_RTU1_IS10032 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Input Status 10032"
  8000 0 MODBUS_RTU1_CS01 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 01"
  8001 0 MODBUS_RTU1_CS02 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 02"
  8002 0 MODBUS_RTU1_CS03 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 03"
  8003 0 MODBUS_RTU1_CS04 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 04"
  8004 0 MODBUS_RTU1_CS05 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 05"
  8005 0 MODBUS_RTU1_CS06 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 06"
  8006 0 MODBUS_RTU1_CS07 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 07"
  8007 0 MODBUS_RTU1_CS08 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 08"
  8008 0 MODBUS_RTU1_CS09 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 09"
  8009 0 MODBUS_RTU1_CS10 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 10"
  8010 0 MODBUS_RTU1_CS11 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 11"
  8011 0 MODBUS_RTU1_CS12 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 12"
  8012 0 MODBUS_RTU1_CS13 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 13"
  8013 0 MODBUS_RTU1_CS14 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 14"
  8014 0 MODBUS_RTU1_CS15 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 15"
  8015 0 MODBUS_RTU1_CS16 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 16"
  8016 0 MODBUS_RTU1_CS17 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 17"
  8017 0 MODBUS_RTU1_CS18 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 18"
  8018 0 MODBUS_RTU1_CS19 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 19"
  8019 0 MODBUS_RTU1_CS20 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 20"
  8020 0 MODBUS_RTU1_CS21 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 21"
  8021 0 MODBUS_RTU1_CS22 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 22"
  8022 0 MODBUS_RTU1_CS23 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 23"
  8023 0 MODBUS_RTU1_CS24 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 24"
  8024 0 MODBUS_RTU1_CS25 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 25"
  8025 0 MODBUS_RTU1_CS26 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 26"
  8026 0 MODBUS_RTU1_CS27 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 27"
  8027 0 MODBUS_RTU1_CS28 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 28"
  8028 0 MODBUS_RTU1_CS29 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 29"
  8029 0 MODBUS_RTU1_CS30 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 30"
  8030 0 MODBUS_RTU1_CS31 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 31"
  8031 0 MODBUS_RTU1_CS32 D OFF/ON 0 0 0 0 E 1 0 1.000000 0.000000 0 1 0 1.00 "Modbus~RTU_1~Coil Status 32"
 11000 0 MODBUS_RTU2_HR40001 A Unit 0 0 0 0 E 1 0 1.000000 0.000000 0 1 1 1.00 "Modbus~RTU_1~Coil Status 32"
... other entries from RTU2 … (this is not a valid line, just a comment)
:::::::::::::Commands:::::::::::::: (this is not a valid line, just a comment)
 90000 7000 MODBUS_RTU1_FSC_7000 D Open/Close 0 0 0 7 E 1 45 1.000000 0.000000 5000 2 1 0.00 "Modbus~RTU_1~Output Single Coil 7000"
 90001 7005 MODBUS_RTU1_PSR_7005 D Unit 0 0 0 7 E 1 48 1.000000 0.000000 40000 2 1 0.00 "Modbus~RTU_1~Output Single Reg 7000"
 90002 7000 MODBUS_RTU2_FSC_7000 D Open/Close 0 0 0 7 E 2 45 1.000000 0.000000 5000 2 1 0.00 "Modbus~RTU_2~Output Single Coil 7000"
 90003 7005 MODBUS_RTU2_PSR_7005 D Unit 0 0 0 7 E 2 48 1.000000 0.000000 40000 2 1 0.00 "Modbus~RTU_2~Output Single Reg 7000"