OSHMI
Open Substation HMI

IEC61850 Client Driver
Configuration Manual

Version 0.3
© 2023 Ricardo L. Olsen

Introduction
This IEC61850 Client driver is based on MZ Automation’s libiec61850 library stack from:
https://github.com/mz-automation/libiec61850
This driver requires the Microsoft .NET 6.0.x 32bits.
Using this driver it is possible to connect OSHMI to “n” IEC61850 servers (IEDs) over TCP/IP.
This driver is not a gateway, it only directs data to OSHMI.
TLS Certificates are not currently supported. Also Goose and Sampled Values are not supported.
Configuration
OSHMI must be configured to use the JSON UDP protocol driver interface on ports 9100/9101 (this is already configured with default installation, see OSHMI Configuration Manual).
The driver config file is c:\oshmi\conf\iec61850_client.conf. This file has the following format:

#server ,NAME ,HOSTNAME ,PORT ,PASSWORD ,READ_INTERVAL_IN_SECONDS ,AUTOTAG,REPORT_INTEGRITY ,BRCB ,URCB
server ,ied1 ,192.168.0.45 ,102 , ,60 ,N ,60 ,Y ,Y

# rcb entries (all unmentioned rcbs will be enabled)
#entry_type ,PATH ,IntegrityInterval ,Enabled
rcb ,DemoMeasurement/LLN0.BR.brcb01 ,90 ,Y

#entry_type ,PATH ,FunctionalConstraint ,SUBSCRIBE ,OSHMI_TAG
tag ,DemoMeasurement/I3pMMXU1.A.phsB.cVal.mag.f ,MX ,N ,I3pMMXU1.A.phsB.cVal.mag.f
tag ,DemoProtCtrl/Obj1XCBR1.Pos.stVal ,ST ,N ,Obj1XCBR1.Pos.stVal
tag ,DemoProtCtrl/Obj1XCBR1.Pos ,ST ,N ,Obj1XCBR1.Pos
tag ,DemoProtCtrl/Obj1CSWI1.Pos ,ST ,N ,Obj1CSWI1.Pos
tag ,DemoProtCtrl/Obj3XCBR2.Pos ,ST ,N ,Obj3XCBR2.Pos
tag ,DemoProtCtrl/Obj1CSWI1.Pos ,CO ,N ,Obj1CSWI1.Pos

… (repeat for more servers)

Fields are comma separated.
To comment a line add a “#” symbol to its beginning.
Empty lines are allowed.

Server parameters
SERVER: a server line must begin with the word “server”.
NAME: Unique descriptive server name. This is for logging support. Preferably keep it short and without spaces. E.g. “IED1”, “TR1Relay87”.
HOSTNAME: server hostname or IP address. E.g. “192.168.0.45”, “server1.localdomain”.
PORT: TCP Port number for the server. E.g. “102”.
PASSWORD: Server password, if required. If not required leave it empty.
READ_INTERVAL: this is the time interval in seconds to requests reading from all tags not found in reports. Tags found in reports will only be updated by reports, other tags will be read by polling.
AUTOTAG: normally keep it as “N”. The “Y” defines an experimental mode that will forward to OSHMI any points found in reports regardless mentioned in the config file.
REPORT_INTEGRITY: default integrity period in seconds for reports.
BRCB: “Y” or “N” to activate or not buffered reports.
URCB: “Y” or “N” to activate or not unbuffered reports.
The subsequent server parameters are not required and reserved for future configuration of TLS certificates.
Report parameters
ENTRY_TYPE: a report line must begin with the word “rcb”.
PATH: path for the IEC61850 report control block name.
E.g. DemoMeasurement/LLN0.BR.brcb01
INTEGRITY_INTERVAL: integrity period in seconds.
ENABLED: “Y” for enabling a report. “N” won’t enable the report. Unmentioned reports will all be enabled (with the default integrity period for the server).
Tag parameters
ENTRY_TYPE: a tag line must begin with the word “tag”.
PATH: path for the IEC61850 tag. For supervised points it is possible to use the complete path like “DemoMeasurement/I3pMMXU1.A.phsB.cVal.mag.f” or the base path like “DemoMeasurement/I3pMMXU1.A.phsB”. When specified the complete path, it won’t be available the qualifier and timestamp for the measurement. For controls (FC=CO), use always the partial path like “DemoProtCtrl/Obj1CSWI1.Pos” (never use complete path like “DemoProtCtrl/Obj1CSWI1.Pos.Oper.ctlVal”). Never use the $ notation like in “DemoProtCtrl/Obj1CSWI1$CO$Pos$Oper$ctlVal”. Spaces are not allowed in IEC61850 paths.
FUNCTIONAL CONSTRAINT: respective FC code for the tag. “CO” for control. Other possibilities: “MX”, “ST”, “CF”, etc.
SUBSCRIBE: reserved for future use, keep it as “N”.
OSHMI TAG: a tag from OSHMI that will store the respective for the IEC61850 tag. Always match analog values (normally FC=MX) with analog points from OSHMI, statuses (FC=ST) with digital tags in OSHMI and controls (FC=CO) with OSHMI command points (OR=7 in point_list.txt). Spaces are not allowed in OSHMI tags, avoid also “~#@/%\,;” and quotes in tag names.

Command Line Arguments
1st Argument: Log level “0” to “3” with increasingly verbosity. Default is level 1.
2nd Argument: “1” or “0” to enable or not full browse of IEC61850 tree for IED’s. This will be slow if enabled, delaying the beginning of scanning. Default is disabled.
e.g.
iec61850_client.exe 3 1 (maximum log level and browse tree)
Remarks
OSHMI tags must be present at point_list.txt or they will be created at run time when first received (at the end of the address space).
To write to IEC61850 tags it must be configured a command tag in point_list.txt (origin=7). Tags with FC not equal to “CO” and complete path like “DemoProtCtrl/Obj1CSWI1.Mod.ctlModel” [CF] will trigger a simple MMS Value write.
All report control blocks (buffered and unbuffered) not mentioned in the config file will be activated by the driver.
The driver will create JSON files in c:\oshmi\conf to keep track of last seen report ids for each server, to avoid undesired replay of already processed reports.

Example point_list.txt
VERSION 3
POINT_NUMB ADDR ID TYP MESSAGE ALM EQ INF OR UN RTU ASDU KCONV1 KCONV2 SUPCMD DC PR INIVAL "SUBEST~BAY~DESCRIPTION"
 200000 0 Obj1CSWI1.Pos D OFF/ON 0 0 0 7 S 0 45 1.0000 0.0000 200004 2 1 0.0000 "IEC61850Ied1~CSWI1~ControlPos"
 200001 0 I3pMMXU1.A.phsB.cVal.mag.f A val 0 0 0 0 E 0 13 1.0000 0.0000 0 1 1 1.0000 "IEC61850Ied1~I3pMMXU1~CurrentPhsBMagF"
 200002 0 I3pMMXU1.A.phsB A val 0 0 0 0 E 0 13 1.0000 0.0000 0 1 1 1.0000 "IEC61850Ied1~I3pMMXU1~CurrentPhsB"
 200003 0 Obj1XCBR1.Pos.stVal D OFF/ON 0 0 0 0 E 0 30 1.0000 0.0000 0 2 2 1.0000 "IEC61850Ied1~XCBR1~PosStVal"
 200004 0 Obj1XCBR1.Pos D OFF/ON 0 0 0 0 E 0 30 1.0000 0.0000 0 2 2 1.0000 "IEC61850Ied1~XCBR1~Pos"
 200005 0 Obj3XCBR2.Pos D OFF/ON 0 0 0 0 E 0 30 1.0000 0.0000 0 2 2 1.0000 "IEC61850Ied1~XCBR2~Pos"